# Arc Flash Risk Assessment

This document can be used by installers as a template for an arc-flash risk assessment required to ensure compliance with IET CoP and PAS63100.  The installer can choose to use this document in its entirety, completing details that require installer input, or they can extract the manufacturer’s supplied data to incorporate into their own document.

**System Type:** Split Inverter + Battery System

**Purpose:** This document provides an arc flash risk assessment. It includes manufacturer-supplied data and sections for installer input to ensure a complete, site-specific assessment in line with IET CoP and PAS 63100.

# Product & System Information

Manufacturer: FoxESS Co., Ltd.

Product Model(s):

Inverter: KH7 KH8 KH9 KH10 KH10.5

Battery: EP series

# Manufacturer Supplied Data

## System Ratings

| Nominal AC Voltage | 220/230V |
| --- | --- |
| Nominal DC Bus Voltage | 360V |
| Maximum Prospective Fault Current (AC) | 103A |
| Maximum Prospective Fault Current (DC) | 28A |
| Internal Short‑Circuit Withstand | Rated current |
| Other Key Ratings | N/A |

## Protective Devices (Internal - Inverter)

| Device Location | Device Type | Rating (A/kA) | Trip/Clearing Time |
| --- | --- | --- | --- |
| Underside of the inverter | DC switch | 45A | Isolator only – no protective function |

## Protective Devices (Internal - Battery)

| Device Location | Device Type | Rating (A/kA) | Trip/Clearing Time |
| --- | --- | --- | --- |
| Battery enclosure | Relay | 100A | ≤100ms |
| Battery enclosure | Fuse | 70A | ≤1ms |

## Arc Flash Baseline Data (Manufacturer‑Supplied)

| Working Distance | Incident Energy (cal/cm²) |
| --- | --- |
| 450mm (typical) | ~6.45 cal/cm² |

# Values provided are manufacturer baseline only; site-specific factors may increase/decrease incident energy.

# Installer Responsibility

Conduct full arc flash risk assessment covering site cabling, grid characteristics, upstream device coordination, and environmental factors.

# Hazard Identification & Risk Assessment

Example values: Likelihood: “Possible”; Severity: “Major”; Initial Risk: “High”

| Task/Area | Potential Hazard | Likelihood | Severity | Initial Risk |
| --- | --- | --- | --- | --- |
| Panel removal (live) | Exposure to DC bus, arc flash risk | Specify | Specify | Specify |
| Cable termination | Arc from incorrect connection | Specify | Specify | Specify |
| Upstream device coordination | Failure leading to arc energy higher than design limits | Specify | Specify | Specify |

# Control Measures

**Design Controls (Manufacturer):** Manufacturer provides DC fuses, labelled enclosures, integrated isolators, and guidance on upstream protective devices (please refer to product manual).

**Administrative Controls (Installer):** Installer to ensure safe isolation procedures, apply live working permits only when absolutely necessary, and follow BS 7671/IET CoP requirements.

**Personal Protective Equipment (PPE):** Installer to specify; example: Arc-rated clothing (e.g.g 8–12 cal/cm²), insulated gloves (e.g. Class 0), full-face arc shield, insulated tools.  Installer must confirm final PPE category based on site-specific study.

# Residual Risk

With correct procedures and PPE, residual risk is Low for normal operation and Medium for live maintenance tasks.

# Emergency Response

Isolate at the main AC and DC isolators. Evacuate area in case of arc flash or fire. Contact emergency services and follow site emergency procedures.

# Sign-Off

Installer Name & Signature: ________________________ Date: ______________